## Summary
PANDA Sub-system name: | Target Spectrometer EMC (Both Endcaps and Barrel)
Controls contact person: | Tobias Triffterer
Hardware | Controls
High Voltage (HV) | YES
Low Voltage (LV) | YES
Front-end electronics (FEE) | YES | Does your Front-End has slow controls parameter like temperatures, voltages, etc.
Gas | YES
Vacuum | NO
Cooling | YES
Movement/Position | NO | Do you have moving parts and need position monitoring? This is not about alignment of the detector!
Others | NO | feel free to add more rows to describe your sub-system
SW and/or HW Interface with | Controls
Software Trigger | NO
Accelerator (HESR) | YES
Other Panda Sub-system(s) | YES | feel free to add more rows to describe your sub-system
Target | YES
Detector Safety System (DSS) | YES

## HV
High Voltage Power Supplies
Used Hardware | iseg EHS modules and crates |  |  |  | Producer / Modell
Communication bus: | CAN bus (newer crates may have Ethernet)
Control software status: | IOC, GUI |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Voltage Measure | DOUBLE | V | 3 | 5 | 0.2 | 4040
Current Measure | DOUBLE | A | 12 | 5 | 1e-09 | 4040
Voltage Set | DOUBLE | V | 3 | on change | 0 | 4040
Current Limit | DOUBLE | A | 12 | on change | 0 | 4040
Channel Status | INT |  |  | 5 | 0 | 4040
Channel Event Status | INT |  |  | 5 | 0 | 4040
Channel Control | INT |  |  | on change | 0 | 4040
Module Status | INT |  |  | 5 | 0 | 505
Module Event Status | INT |  |  | 5 | 0 | 505
Module Control | INT |  |  | on change | 0 | 505
Module Temperature | DOUBLE | °C | 1 | 5 | 1 | 505

## LV
Low Voltage Power Supplies
Used Hardware | Wiener PL512 |  |  |  | Producer / Modell
Communication bus: | SNMP/Ethernet
Control software status: | IOC, GUI |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Voltage Measure | DOUBLE | V | 3 | 5 | 0.2 | to be determined
Voltage Sense | DOUBLE | V | 3 | 5 | 0.2 | to be determined
Current Measure | DOUBLE | A | 2 | 5 | 0.2 | to be determined
Voltaget Set | DOUBLE | V | 3 | on change | 0 | to be determined
Current Limit | DOUBLE | A | 2 | on change | 0 | to be determined
Channel Status | INT |  |  | 5 | 0 | to be determined
Channel Control | INT |  |  | on change | 0 | to be determined
Temperature | DOUBLE | °C | 1 | 5 | 1 | to be determined

## FEE
Used Hardware | Custom (THMP, LED Pulser, EMC ADCs, HV-Trimmer)
Communication bus: | CAN for THMP and LED Pulser, ADC and Trimmer not yet decided
Control software status: | IOC + GUI for THMP and LED Pulser, ADC and Trimmer nothing yet |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Temperature | DOUBLE | °C | 4 | 5 | 0.02 | 1300
Humidity | DOUBLE | %RH | 1 | 5 | not yet decided | not yet decided
Pressure | DOUBLE | mbar | ?? | 5 | not yet decided | not yet decided
LED Pulser Control | INT |  | 0 | on change | 0 | 10
LED Pulser Frequency | INT | Hz | 0 | on change | 0 | 10
LED Pulser Intensity | INT | ‰ | 0 | on change | 0 | 10
LED Pulser Cycles | INT |  | 0 | on change | 0 | 10
DACs and Switches | INT |  | 0 | on change | 0 | 90880
APFEL Power Switch | INT |  | 0 | on change | 0 | 11030
Recovery LED Power | INT |  | 0 | on change | 0 | 2880
Note: Number of LED Pulsers for Barrel and Bachward Endcap not decided, yet.

## Gas
Mass Flow Controller
Mass Flow meter
Pressure Controller
Pressure meter
Safety valve
Temperature sensing
Humidity sensing
Gas analyzer
Other
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
The EMC will be flushed with dry air to prevent the formation of ice.
The pressure inside the EMC will be monitored by the FEE, additional hardware like a gas analyzer is not necessary for air.

## Vacuum
Pumps
Gauges
Valves
Safety Valves
Gas analyzer
Mass spectrometer
Controller
Other
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Cooling
Used Hardware | not yet decided
Communication bus: | not yet decided – depends on manufacturer
Control software status: | nothing yet |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
The cooling system for the target EMC has not been built yet, and no plans have been made.
There is a small system that is only capable of cooling the forward endcap and one barrel slice.
In the final PANDA setup, there will be a common system for the whole target EMC. As no plans exist for this system at the moment, no information can be given here.

## Positioning
Used Hardware
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Others
Used Hardware
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Software Trigger
Interface with PANDA Software trigger
Brief description of the information planned to be exchanged with the online software trigger:
Configuration database or flags indicating the hardware configuration of your FEE, HV, LV, etc:

## HESR
Interface with HESR
Brief description of the information planned to be exchanged with the accelerator: What type of information are you planning to share with the HESR ?
Note: HESR status = > filling, ramping, tuning, stable beams will be available to ALL PANDA sub-systems via Central DCS; HESR beam parameters => current, energy, etc will be available to ALL PANDA sub-systems via Central DCS.
Data available via central DCS should be sufficient.

## Other PANDA Sub-Systems
Interface with Other PANDA Sub-system
Brief description of the information planned to be exchanged with other PANDA sub-system(s)
It may be necessary to exchange temperature or power consumption information with subsystems mounted directly to the EMC.

## DSS
Detector Safety System
No. of HW Interlocks | 3
Please indicate for each interlock: Condition(s) when the interlock is generated and which equipment is going to be switched off or in standby
1) If the detector is open and people are working there, it has to be impossible to switch on the HV to comply with electrical safety regulations. 2) If there is a leak in the cooling circuit or the flow in there is too small, the cooling compressor has to be switched off to prevent damage. In case of a leakage, safety valves will be closed in addition. 3) If the internal temperature in a HV or LV power supply is too high, this power supply has to be switched off. If the current measurement indicates a short circuit, this HV/LV channel has to be switched off.