## Summary
PANDA Sub-system name: | MVD
Controls contact person: | Hans_Georg Zaunick (TO BE CONFIRMED!)
Hardware | Controls
High Voltage (HV) | YES
Low Voltage (LV) | YES
Front-end electronics (FEE) | YES | Does your Front-End has slow controls parameter like temperatures, voltages, etc.
Gas | YES
Vacuum | YES
Cooling | YES
Movement/Position | YES | Do you have moving parts and need position monitoring? This is not about alignment of the detector!
Others | NO | feel free to add more rows to describe your sub-system
SW and/or HW Interface with | Controls
Software Trigger | YES
Accelerator (HESR) | YES
Target | YES | feel free to add more rows to describe your sub-system
Magnet | YES
STT | YES
BEMC | YES
Detector Safety System (DSS) | YES

## HV
High Voltage Power Supplies
STRIP PART
Used Hardware | ISEG |  |  |  | Producer / Modell
Communication bus: | Ethernet/CAN/USB
Control software status: | Graphycal user interface (?) |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Set Voltage |  | Volt | 0.1 | 2 s | 0.5 | 296
Read Voltage |  | Volt | 0.1 | 2 s | 0.5 | 296
Set Current |  | nAmpere | 10 | 2 s | 100 | 296
Read Current |  | nAmpere | 10 | 2 s | 100 | 296
Ramp |  | Volt/sec | 0.1 | N/A | N/A | 296
Channel Status |  |  |  | 2 s | 0 | 296
Channel Control |  |  |  | on change | 0 | 296
Ramp status |  |  |  | 2 s | 0 | 296
Ramp control |  |  |  | on change | 0 | 296
Temperature ?
PIXEL PART
Used Hardware | CAEN SY4527 |  |  |  | Producer / Modell
Communication bus: | Ethernet/USB
Control software status: | Graphycal user interface (?) |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Set Voltage |  | Volt | 0.1 | 2 s | 0.5 | 176
Read Voltage |  | Volt | 0.1 | 2 s | 0.5 | 176
Set Current |  | nAmpere | 10 | 2 s | 100 | 176
Read Current |  | nAmpere | 10 | 2 s | 100 | 176
Ramp |  | Volt/sec | 0.1 | N/A | N/A | 176
Channel Status |  |  |  | 2 s | 0 | 176
Channel Control |  |  |  | on change | 0 | 176
Ramp status |  |  |  | 2 s | 0 | 176
Ramp control |  |  |  | on change | 0 | 176
Temperature ?

## LV
Low Voltage Power Supplies
STRIP PART
Used Hardware | Wiener MPOD |  |  |  | Producer / Modell
Communication bus: | Ethernet/CAN/USB
Control software status: | Graphical user interface (?) |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Set Voltage |  | V | 0.1 | 2 s | 0.5 | 676
Read Voltage |  | V | 0.1 | 2 s | 0.5 | 676
Set Current |  | mA | 1 | 2 s | 100 | 676
Read Current |  | mA | 1 | 2 s | 100 | 676
Ramp |  | Volt/sec | 0.1 | N/A | N/A | 676
Channel status |  |  |  | 2 s | 0 | 676
Channel control |  |  |  | on change | 0 | 676
Ramp status |  |  |  | 2 s | 0 | 676
Ramp control |  |  |  | on change | 0 | 676
Temperature ?
PIXEL PART &MVD services
Used Hardware | CAEN SY4527 |  |  |  | Producer / Modell
Communication bus: | Ethernet/CAN/USB
Control software status: | Graphical user interface (?) |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
Set Voltage |  | V | 0.1 | 2 s | 0.5 | 976
Read Voltage |  | V | 0.1 | 2 s | 0.5 | 976
Set Current |  | mA | 1 | 2 s | 100 | 976
Read Current |  | mA | 1 | 2 s | 100 | 976
Ramp |  | Volt/sec | 0.1 | N/A | N/A | 976
Channel status |  |  |  | 2 s | 0 | 976
Channel control |  |  |  | on change | 0 | 976
Ramp status |  |  |  | 2 s | 0 | 976
Ramp control |  |  |  | on change | 0 | 976
Temperature ?

## FEE
Used Hardware | MVD data concentrator - tbd
Communication bus: | tbd
Control software status: | tbd |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels
STRIP
1 pasta: 64 ch x 41 bit local + 212 bit global
tot: 2836 bit /pasta
3112 pasta +296 mdc
9.67 Mbit for all pasta and mdc.
with exclusion of GBT for the strip part……..
PIXEL
1 TOPIX: 12760 ch x 12 Bit
tot: 153120 bit/ ToPix
810 topix
124 Mbit for all ToPix asics
with exclusion GBT for the pixel part……..

## Gas
Mass Flow Controller
Mass Flow meter
Pressure Controller
Pressure meter
Safety valve
Temperature sensing
Humidity sensing
Gas analyzer
Other
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Vacuum
Pumps
Gauges
Valves
Safety Valves
Gas analyzer
Mass spectrometer
Controller
Other
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Cooling
Used Hardware | Schneider PLC (ex.) MODICON (Not yet defined (example from a similar cooling plant). See details of the controled hardware, below
Communication bus: | Ethernet, CanBus, MODbus
Control software status: | graphical user interface (?) |  |  |  | Simple terminal/script communication, graphical user interface, other
Hardware | Commercial Name/Type | No. of channels
Return Valve |  | 85
Mass Flow meter | KOBOLD | 85
Pressure regulator | ALICAT Series PCR | 85
Relative pressure | Huba control (type 691) | 3
Pressure meter | HBM | 85
Pressure sensor |  | 170
Safety valve (pneumatic) | SWAGELOK SS-12BK-MM1C | 180
SWAGELOK SS-12BK-MM-10
Temperature sensors | thermorest Pt100 | 90
Humidity sensing |  | 10
Vacuum pump |  | 1
Chiller | SAUTER VXN | 1
Water cleaning unit |  | 1
Inlet pump |  | 1
Tank level indicator | BURKERT 8170 | 1
Heater exchanger |  | 1
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Positioning
Used Hardware
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Others
Used Hardware
Communication bus:
Control software status: |  |  |  |  | Simple terminal/script communication, graphical user interface, other
List of Parameters
Parameter | Type [INT¦DOUBLE¦STRING] | Units | Precision | Time resolution | Archive Deadband | Number of channels

## Software Trigger
Interface with PANDA Software trigger
Brief description of the information planned to be exchanged with the online software trigger:
Status of the MVD parts
Configuration database or flags indicating the hardware configuration of your FEE, HV, LV, etc:
Flags: Strip Barrels (on/off), Strip Disk (on/off), Pixel Barrels (on/off), Pixel Disks (on/off)

## HESR
Interface with HESR
Brief description of the information planned to be exchanged with the accelerator: What type of information are you planning to share with the HESR ?
Note: HESR status = > filling, ramping, tuning, stable beams will be available to ALL PANDA sub-systems via Central DCS; HESR beam parameters => current, energy, etc will be available to ALL PANDA sub-systems via Central DCS.
In addition to the HESR status and HESR beam parameters available via central DCS, MVD would like a fast information of beam lost

## Other PANDA Sub-Systems
Interface with Other PANDA Sub-system
Brief description of the information planned to be exchanged with other PANDA sub-system(s)
Magnet | B on/off | no HW
Target | switched on/off | no HW
STT cooling | switched on/off | no HW
STT supply | switched on/off | no HW
BWE cooling | switched on/off | no HW
BWE supply | switched on/off | no HW

## DSS
Detector Safety System
No. of HW Interlocks | Condition with negative logic to avoird problem if all systems are stopped because of a lack of powering | Feedback on:
1- Interlock cooling vs LV and HV - strip (&service) | interlock: signal on - the cooling is swithched on, temperatures and pressures are correct | Strip LV power supplies switched on and Strip HV power suppl. switched on
| interlock: signal off - the cooling is swithched off or the temperature of the system is not still reached and stabilized | Strip LV power supplies switched off and Strip HV power suppl. switched off
| interlock: signal off - the electrical current is switched off in the coopling plant and not in the power supplies racks | Strip LV power supplies switched off and Strip HV power suppl. switched off
1- Interlock cooling vs LV and HV - pixel (&service) | interlock: signal on - the cooling is swithched on, temperatures and pressures are correct | Pixel LV power supplies switched on and Strip HV power suppl. switched on
| interlock: signal off - the cooling is swithched off or the temperature of the system is not still reached and stabilized | Pixel LV power supplies switched off and Strip HV power suppl. switched off
| interlock: signal off - the electrical current is switched off in the coopling plant and not in the power supplies racks | Pixel LV power supplies switched off and Strip HV power suppl. switched off
1-Interlock from fire alarm (HESR hall) | interlock: signal on - the MVD is on | Strip and Pixel
| interlock: signal off - the MVD is off | Strip and Pixel
1- Interlock general safety system of PANDA
Please indicate for each interlock: Condition(s) when the interlock is generated and which equipment is going to be switched off or in standby